## Sheet 1
Budget for acquisition of advanced and environment-friendly plant for production wastewater technological treatment
Name of the Contracting Project Promotor: | DRACO D.O.O.
Address: | Draškovićeva 4, 21210, Solin, Croatia
VAT no. | 08658331098
Contact person: | Ante Jukić
Contact person e-mail: | ante.jukic@dracopro.com
Name of the Programme: | Business Development and Innovation Croatia
Name of the project: | Greening of production process
Bid selection criteria: | Lowest price
Procurement number: | 2022/340872-01
Description | Unit of measure | Quantity | Currency (EUR) | Price per unit of measure (VAT excluded) | Total price (VAT excluded)
Advanced and environment-friendly plant for wastewater technological treatment The system must be based on vacuum evaporation (or equivalent) procedure and must have following characteristics: - Compact design for easy installation and easy access to the device - Low temperature based process = low contact temperature thanks to the high level of vacuum and heat pump technology (distillate output temperate 20°C+/- 1°C, boiling point temperature 35°C+/-1°C - 40°C+/-1°C) - Piping, valves, pumps and any flanged component should have adequate sealing over time, and access for easy intervention (when needed) - FAT (or equivalent) is supplied with the system - Easy access to internal parts - Automated foam control system - Superconcentration system for obtaining semi-solid or dry concentrate - Touch panel with display of functions and operating settings that can be monitored and changed - Possibility of program maintenance - Fully automated process - HMI Siemens (or equivalent) control system - Simple display and access to control functions - Possibility of remote monitoring - Monitoring of pressure, temperature and other values with analog control - Visualization of values on the HMI screen - Certified materials - Certificate for every type of welding - Guarantee of traceability of the material used (eg: 10204: 3.1 for stainless steel (or equivalent)) - High accuracy according to the production standard in accordance with the strictest regulations (IS0 EN 3834; or equivalent) - Quality check during production (NDT (or equivalent) on welding, individual check of each boiler and element under pressure) by issuing special certificates (PED Directive for pressure equipment - or equivalent) Technical requirements: - Device capacity 500 l+/-0,5 l/day - Distillate capacity 21 l/h +/-0,5 l - Total capacity in 24 hours 500 l/day +/-0,5 l - Installed power 6.2 kW +/- 5% - Connection 400/3/50 +/-1% - Compressed air 7 bar +/-0,2 bar - Dimensions (length x width x height) - 2600 x 1600 x 2300 mm +/- 5% - Built-in dimensions (length x width x height) - 4000 x 2800 x 2500 mm +/- 0,1% - Working level 200 L +/-0,5 L Basic connections - Waste water connection 1" +/- 0,2% - Distillate output ½" +/- 0,2% - Concentrate outlet 2" +/- 0,2% - Compressed air Ø8 mm+/- 0,1% - Clean water connection ½" +/- 0,2% - Antifoam connector ½" +/- 0,2% Material quality requirements - The material and equipment to be installed must meet the standards. For all devices, appropriate certificates are delivered within the equipment. - The material (from which the system is made) must have an accompanying guarantee for the material used (e.g. 10204:3.1 for SST - or equivalent), high accuracy according to production standard ISO EN 3834 - or equivalent, control quality during production (NDT - or equivalent on welding) possessing specific certificates (PED - or equivalent). - Boiling vessel: AISI 316 certified (or equivalent) - Heat exchanger AISI316/316L certified (or equivalent) - Base: Reinforced base AISI 304 (or equivalent) - PLC and operational panel: Siemens (or equivalent) - Valves: AISI 316 (or equivalent) - Connecting pipelines: PVDF/PVC (or equivalent) - Distillate tank: AISI 316 (or equivalent) - Cable glands: PVC (or equivalent) - Condensation exchanger: AISI 316L (or equivalent) - Vacuum circuit: 1.4401/1.4404/PVC/FPM (or equivalent) - Vacuum pump: AISI 316 (or equivalent) - Vacuum valves: PVC/FPM (or equivalent) Operational conditions - Max product inlet temperature: 10-30°C +/- 1°C - Outlet temperature of the distillate: 15-20°C +/- 1°C - Outlet temperature of the concentrate: 35-40°C +/- 1°C Mandatory documentation: - Instruction manual (or equivalent) - CE certificate (or equivalent) - Floor plan with dimensions (or equivalent) - Flow charts (or equivalent) - Hydraulic and pneumatic P&ID (or equivalent) - Electrical diagram (or equivalent) - Manuals on the main components (or equivalent) The system must comply with current regulations and Croatian standards, as well as other standards in areas not covered by Croatian standards (EN, DIN, VDI, BS, ISO; or equivalent to them) The system must reach following outputs: - Reduce at least 90% +/-5% of whole waste water quantity - Reduce at least 95% +/-5% of KpK (chemical oxygen demand) - Output quality (destillate) must be adequate for re-use in technical process | set | 1
Total price VAT excluded
VAT
Total price VAT included
______________________________
|  | Place of seal |  | signature of the authorized person
|  | Place and date |  | ______________________________